# List of Safe Work Practices

# Fire Protection and Prevention
Safe Work Practices

[Company name] will take all necessary steps to prevent fires. Inspections during various operations will be made to assure fire-prevention objectives are being met. The steps are listed below.

Reporting and Extinguishing a Fire

-The fire department and area supervisor will be notified when a fire is spotted.

-All workers will be alerted and evacuated as needed.

-The PASS method will be used to extinguish the fire by those employees who have been   properly trained.

-The area will be evacuated immediately if the fire is large.

Fire Protection

-Before each project begins, the project manager or designee will contact the local fire department and determine whether any variations from the company’s standard fire-prevention procedures are required.

-No-smoking signs will be posted in all regulated areas.

-Only approved containers will be used to store flammable or combustible materials.

-All containers will be bonded together and grounded when transferring flammable or combustible liquids.

-All work areas will be kept free of debris and other combustible materials.

-Inside company-owned or leased buildings, fire extinguishers will be spaced no more than 100 feet apart and will have no less than a 2A rating for every 3,000 feet of protected building.

-All employees will be trained on the use of fire extinguishers initially upon hire and annually thereafter.

-No employee will be permitted to use an extinguisher without having been fully trained.

-Fire extinguishers will not be stored at a distance greater than 30 feet from torch users.

-A fire extinguisher, rated not less than 10B, will be provided within 50 feet of the location where more than 5 gallons of combustible liquids or 5 pounds of a flammable gas are used on a job site.

-Fire extinguishers will not be stored at a distance greater than 10 feet from a liquid petroleum gas (LPG) cylinder.

-Mops will be “spun out” and placed on a noncombustible surface at the end of each day on projects involving hot bitumen.

-A fire watch will be posted for one hour after work has concluded for torch-applied roof systems or other hot work.

Flammable and Combustible Liquid Storage

-No more than 25 gallons of flammable and combustible liquids will be stored outside approved safety cabinets.

-No more than 60 gallons of flammable liquids will be stored inside an approved safety cabinet.

-Combustible liquids will not exceed 120-gallon capacity inside approved safety cabinets.

-The number of approved safety cabinets in one room will not exceed three.

-Gasoline will not be used as a solvent for cleaning.

-All containers will be labeled in accordance with Occupational Safety and Health Administration’s (OSHA’s) Hazard Communication Standard.

-Buildings or structures containing flammable liquids or gases must be constructed of fire-resistant material.

-Flammable liquids or gases will be kept away from heat and from welding or any other operation involving flames or sparks.

Handling Flammable Gases

-LPG cylinders will be placed on a firm foundation and secured in an upright position.

-All LPG cylinders will be equipped with valve-protection devices.

-LPG cylinders will not be stored closer than 10 feet to the kettle.

-LPG cylinders will be placed away from vehicular traffic.

-LPG cylinders will not be stored inside buildings.

-Acetylene bottles will be stored in the upright position and secured.

-When in transport or not in use, acetylene bottles will have caps in place.

Oxygen cylinders must be stored at least 20 feet from acetylene cylinders.

Handling Flammable and Combustible Liquids

-During refueling operations, all engines and motors will be turned off and allowed to cool.

-No smoking will be permitted during the fueling process.

-No flammable liquid or gas will be used unless it has been positively identified beforehand.

-Health and physical hazards will be communicated to employees in accordance with OSHA’s Hazard Communication Standard before the product is used.

-When flammable liquids and gases are being transported, all Department of Transportation rules will be followed.

Fire Extinguishers

-In buildings, all fire extinguishers will be mounted and properly marked.

-All vehicles will carry at least one 20-pound ABC-rated extinguisher.

-When at a job site, all employees will know the location of each fire extinguisher.

-Before using an extinguisher, all employees will be trained and familiar with the PASS method of fire fighting.

-Each fire extinguisher will be inspected monthly to make sure it is in its designated location and has not been tampered with or actuated.

-No fire extinguisher will be stored on the ground.

-Each fire extinguisher will be clearly visible with nothing obstructing or obscuring it from view.

-All fire extinguishers will be examined at least yearly and/or recharged or repaired to ensure operability and safety.  A tag must be attached to show the maintenance or recharge date and signature or initials of the person performing the service.